## Sheet1
Value | OBIS reference | Name | Attribute | Class ID | Value Format | Value Unit
Header information | - | - | - | - | Manufacturer specific
Version information for P1 output | 1-3:0.2.8.255 | version | 2 | 1 Data | S2, tag 9
Date-time stamp of the P1 message | 0-0:1.0.0.255 | timestamp | 2 | 8 | TST | YYMMDDhhmmssX
Equipment identifier | 0-0:96.1.1.255 | meterEquipmentId | 2 Value | 1 Data | Sn (n=0..96), tag 9
Meter Reading electricity delivered to client (Tariff 1) in 0,001 kWh | 1-0:1.8.1.255 | meterToT1 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
Meter Reading electricity delivered to client (Tariff 2) in 0,001 kWh | 1-0:1.8.2.255 | meterToT2 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
Meter Reading electricity delivered by client (Tariff 1) in 0,001 kWh | 1-0:2.8.1.255 | meterFromT1 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
Meter Reading electricity delivered by client (Tariff 2) in 0,001 kWh | 1-0:2.8.2.255 | meterFromT2 | 2 Value | 3 Register | F9(3,3), tag 6 | kWh
Tariff indicator electricity. The tariff indicator can also be used to switch tariff dependent loads e.g boilers. This is the responsibility of the P1 user | 0-0:96.14.0.255 | currentTariff | 2 Value | 1 Data | S4, tag 9
Actual electricity power delivered (+P) in 1 Watt resolution | 1-0:1.7.0.255 | actualPowerDelivered | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Actual electricity power received (-P) in 1 Watt resolution | 1-0:2.7.0.255 | actualPowerReceived | 2 Value | 3 Register | F5(3,3), tag 18 | kW
The actual threshold Electricity in kW | 0-0:17.0.0.255 | actualThreshold | 3 Threshold active | 71 Limiter Class | F4(1,1), tag 18 | kW
Switch position Electricity (in/out/enabled). | 0-0:96.3.10.255 | electicitySwitchPos | 3 Control State | 70 Disconnector Control | I1, tag 22
Number of power failures in any phase | 0-0:96.7.21.255 | totalPowerFailures | 2 Value | 1 Data | F5(0,0), tag 18
Number of long power failures in any phase | 0-0:96.7.9.255 | totalLongPowerFailures | 2 Value | 1 Data | F5(0,0), tag 18
Power Failure Event Log (long power failures) | 1-0:99.97.0.255 | powerFailureLog | 2 Buffer | 7 Profile Generic | TST, F10(0,0) - tag 6 Format applicable for the value within the log (OBIS code 1-0:96.7.19.255) | Timestamp (end of failure) –duration in seconds
Number of voltage sags in phase L1 | 1-0:32.32.0.255 | voltageSagsL1 | 2 Value | 1 Data | F5(0,0), tag 18
Number of voltage sags in phase L2 (polyphase meters only) | 1-0:52.32.0.255 | voltageSagsL2 | 2 Value | 1 Data | F5(0,0), tag 18
Number of voltage sags in phase L3 (polyphase meters only) | 1-0:72.32.0.255 | voltageSagsL3 | 2 Value | 1 Data | F5(0,0), tag 18
Number of voltage swells in phase L1 | 1-0:32.36.0.255 | voltageSwellsL1 | 2 Value | 1 Data | F5(0,0), tag 18
Number of voltage swells in phase L2 (polyphase meters only) | 1-0:52.36.0.255 | voltageSwellsL2 | 2 Value | 1 Data | F5(0,0), tag 18
Number of voltage swells in phase L3 (polyphase meters only) | 1-0:72.36.0.255 | voltageSwellsL3 | 2 Value | 1 Data | F5(0,0), tag 18
Text message codes: numeric 8 digits | 0-0:96.13.1.255 | textMessageCode | 2 Value | 1 Data | Sn (n=0..16),, tag 9
Text message max 1024 characters. | 0-0:96.13.0.255 | textMessageText | 2 Value | 1 Data | Sn (n=0..2048), tag 9
Device-Type | 0-n:24.1.0.255 | deviceType | 9 Device type | 72 M-Bus client | F3(0,0), tag 17
Instantaneous current L1 in A resolution. | 1-0:31.7.0.255 | instCurrentL1 | 2 Value | 3 Register | F3(0,0), tag 18 | A
Instantaneous current L2 in A resolution. | 1-0:51.7.0.255 | instCurrentL2 | 2 Value | 3 Register | F3(0,0), tag 18 | A
Instantaneous current L3 in A resolution. | 1-0:71.7.0.255 | instCurrentL3 | 2 Value | 3 Register | F3(0,0), tag 18 | A
Instantaneous active power L1 (+P) in W resolution | 1-0:21.7.0.255 | instActPowerPlusL1 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instantaneous active power L2 (+P) in W resolution | 1-0:41.7.0.255 | instActPowerPlusL2 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instantaneous active power L3 (+P) in W resolution | 1-0:61.7.0.255 | instActPowerPlusL3 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instantaneous active power L1 (-P) in W resolution | 1-0:22.7.0.255 | instActPowerMinL1 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instantaneous active power L2 (-P) in W resolution | 1-0:42.7.0.255 | instActPowerMinL2 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Instantaneous active power L3 (-P) in W resolution | 1-0:62.7.0.255 | instActPowerMinL3 | 2 Value | 3 Register | F5(3,3), tag 18 | kW
Equipment identifier (Gas) | 0-n:96.1.0.255 | equipmentId | 2 Value | 1 Data | Sn (n=0..96), tag 9
Last hourly value (temperature converted), gas delivered to client in m3, including decimal values and capture time | 0-n:24.2.1.255 | lastReading | 5 Capture time | 4 Extended Register | TST
Last hourly value (temperature converted), gas delivered to client in m3, including decimal values and capture time | 0-n:24.2.1.255 | lastReading | 2 Value | 4 Extended Register | F8(2,2)/F8(3,3), tag 18 (See note 2) | m3
Valve position Gas (on/off/released). (See Note 3) | 0-n:24.4.0.255 | valvePos | 3 Control state | 70 Disconnect Control | I1, tag 22
Device-Type | 0-n:24.1.0.255 | deviceType | 9 Device type | 72 M-Bus client | F3(0,0), tag 17
Equipment identifier (Thermal: Heat or Cold) | 0-n:96.1.0.255 | equipmentId | 2 Value | 1 Data | Sn (n=0..96), tag 9
Last hourly Meter reading Heat or Cold in 0,01 GJ and capture time | 0-n:24.2.1.255 | lastReading | 5 Capture time | 4 Extended Register | TST
Last hourly Meter reading Heat or Cold in 0,01 GJ and capture time | 0-n:24.2.1.255 | lastReading | 2 Value | 4 Extended Register | Fn(2,2) (See note 1) | GJ
Valve position (on/off/released). (See Note 3) | 0-n:24.4.0.255 | valvePos | 3 Control state | 70 Disconnect Control | I1, tag 22
Device-Type | 0-n:24.1.0.255 | deviceType | 9 Device type | 72 M-Bus client | F3(0,0), tag 17
Equipment identifier (Water) | 0-n:96.1.0.255 | equipmentId | 2 Value | 1 Data | Sn (n=0..96), tag 9
Last hourly Meter reading in 0,001 m3 and capture time | 0-n:24.2.1.255 | lastReading | 5 Capture time | 4 Extended Register | TST
Last hourly Meter reading in 0,001 m3 and capture time | 0-n:24.2.1.255 | lastReading | 2 Value | 4 Extended Register | Fn(3,3) (See Note 1) | m3
Valve position (on/off/released).(See Note 3) | 0-n:24.4.0.255 | valvePos | 3 Control state | 70 Disconnect Control | I1, tag 22
Device-Type | 0-n:24.1.0.255 | deviceType | 9 Device type | 72 M-Bus client | F3(0,0), tag 17
Equipment identifier | 0-n:96.1.0.255 | equipmentId | 2 Value | 1 Data | Sn (n=0..96), tag 9
Last hourly Meter reading and capture time (e.g. slave E meter) | 0-n:24.2.1.255 | lastReading | 5 Capture time | 4 Extended Register | TST
Last hourly Meter reading and capture time (e.g. slave E meter) | 0-n:24.2.1.255 | lastReading | 2 Value | 4 extended Register | Fn(3,3) (See Note 1) | kWh
Valve/Switch position (on/off/released). (See Note 3) | 0-n:24.4.0.255 | valvePos | 3 Control state | 70 Disconnect Control | I1, tag 22